## Voc>15kV
Dados de Entrada |  |  |  | Resultado | [5 empty] | Comparação
[10 empty] | Média Todos | 97.02% | Média OSHA | 0.4413%
|  |  |  | Fonte | Metodologia | Energia Incidente | Limite Seguro de Aproximação | Software dos Autores |  | DP Todos | 111.3% | DP OSHA | 1.002%
Equipamento | Tensão Nominal [kV] | Icc [kA] | TIcc [ms] |  |  |  |  | Energia Incidente | Limite Seguro de Aproximação | Erro Percentual Energia Incidente | Erro Percentual no Limite Seguro de Aproximação
Pátio SE 230 | 230 | 30 | 166 | O Setor Eletrico Ed.198 | OSHA 1910.269 App E | 5 | 1720 | 4.98 | 1720 | 0.4% | 0%
Pátio SE 230 | 230 | 30 | 166 | O Setor Eletrico Ed.198 | ArcPro | 4.39 | 1720 | 4.98 | 1720 | 13.44% | 0%
Pátio SE 230 | 230 | 30 | 166 | O Setor Eletrico Ed.198 | EPRI | 3.99 | 1720 | 4.98 | 1720 | 24.81% | 0%
Pátio SE 230 | 230 | 30 | 166 | O Setor Eletrico Ed.198 | EPRI com Coe ciente | 6.34 | 1720 | 4.98 | 1720 | 21.45% | 0%
BARRA750A | 750 | 12 | 133 | Relatório de uma Subestação Real | OSHA 1910.269 App E | 4 | 4830 | 4 | 4830 | 0% | 0%
Pátio SE 138 | 138 | 30 | 183 | O Setor Eletrico Ed.197 | OSHA 1910.269 App E | 6.11 | 1160 | 6.2743 | 1160 | 2.689% | 0%
Pátio SE 138 | 138 | 30 | 183 | O Setor Eletrico Ed.197 | ArcPro | 6.4 | 1160 | 6.2743 | 1160 | 1.964% | 0%
Pátio SE 138 | 138 | 30 | 183 | O Setor Eletrico Ed.197 | ArcCalc | 5.91 | 1160 | 6.2743 | 1160 | 6.164% | 0%
Pátio SE 138 | 138 | 30 | 183 | O Setor Eletrico Ed.197 | Heat Flux | 5.92 | 1160 | 6.2743 | 1160 | 5.985% | 0%
Linha Transmissão 115kV | 115 | 22.147 | 83 | Marroquin; Rehman; Madani.High-Voltage Arc Flash Assessment and Applications—Part 2 set, 2019 | ArcPro | 0.888 | NA | 3.32 | 1020 | 273.9%
Linha Transmissão 115kV | 115 | 22.147 | 83 | Marroquin; Rehman; Madani.High-Voltage Arc Flash Assessment and Applications—Part 2 set, 2019 | Duke HFC | 1.098 | NA | 3.32 | 1020 | 202.4%
Linha Transmissão 115kV | 115 | 45.298 | 83 | Marroquin; Rehman; Madani.High-Voltage Arc Flash Assessment and Applications—Part 2 set, 2019 | ArcPro | 2.141 | NA | 6.64 | 1020 | 210.1%
Linha Transmissão 115kV | 115 | 45.298 | 83 | Marroquin; Rehman; Madani.High-Voltage Arc Flash Assessment and Applications—Part 2 set, 2019 | Duke HFC | 1.922 | NA | 6.64 | 1020 | 245.5%
Linha Transmissão 115kV 25% | 115 | 23.439 | 99 | Marroquin; Rehman; Madani.High-Voltage Arc Flash Assessment and Applications—Part 2 set, 2019 | ArcPro | 1.139 | NA | 3.96 | 1020 | 247.7%
Linha Transmissão 115kV 25% | 115 | 23.439 | 99 | Marroquin; Rehman; Madani.High-Voltage Arc Flash Assessment and Applications—Part 2 set, 2019 | Duke HFC | 0.976 | NA | 3.96 | 1020 | 305.7%
Linha Transmissão 115kV 50% | 115 | 18.701 | 99 | Marroquin; Rehman; Madani.High-Voltage Arc Flash Assessment and Applications—Part 2 set, 2019 | ArcPro | 0.871 | NA | 2.376 | 1020 | 172.8%
Linha Transmissão 115kV 50% | 115 | 18.701 | 99 | Marroquin; Rehman; Madani.High-Voltage Arc Flash Assessment and Applications—Part 2 set, 2019 | Duke HFC | 0.925 | NA | 2.376 | 1020 | 156.9%
Linha Transmissão 115kV 75% | 115 | 18.45 | 99 | Marroquin; Rehman; Madani.High-Voltage Arc Flash Assessment and Applications—Part 2 set, 2019 | ArcPro | 0.851 | NA | 2.376 | 1020 | 179.2%
Linha Transmissão 115kV 75% | 115 | 18.45 | 99 | Marroquin; Rehman; Madani.High-Voltage Arc Flash Assessment and Applications—Part 2 set, 2019 | Duke HFC | 0.912 | NA | 2.376 | 1020 | 160.5%
BARRA230A | 230 | 3.41 | 66 | Relatório de uma Subestação Real | OSHA 1910.269 App E | 4 | 1720 | 4 | 1720 | 0% | 0%
BARRA230B | 230 | 3.41 | 66 | Relatório de uma Subestação Real | OSHA 1910.269 App E | 4 | 1720 | 4 | 1720 | 0% | 0%
BARRA138A | 138 | 3.41 | 76 | Relatório de uma Subestação Real | OSHA 1910.269 App E | 4 | 1160 | 4 | 1160 | 0% | 0%
BARRA138B | 138 | 3.41 | 76 | Relatório de uma Subestação Real | OSHA 1910.269 App E | 4 | 1160 | 4 | 1160 | 0% | 0%

## 208<Voc<15kV
Dados de Entrada | [12 empty] | Resultado |  |  |  |  | Comparação
[18 empty] | Media Todos | 0.2625%
[13 empty] | Fonte | Energia Incidente | Limite Seguro de Aproximação | Software dos Autores |  | DP Todos | 0.5374%
Equipamento | Tensão Nominal [kV] | Configuração dos Eletrodos | Altura [mm] | Largura [mm] | Profundidade [mm] | Icc [kA] | Iarc [kA] | Iarc Mínimo [kA] | Tiarc [ms] | Tiarmin [ms] | Distância entre fases [mm] | Distancia de Trabalho [mm] |  |  |  | Energia Incidente | Limite Seguro de Aproximação | Erro Percentual Energia Incidente | Erro Percentual no Limite Seguro de Aproximação
QDN1 | 0.22 | HCB | 2280 | 650 | 380 | 7.7 | 3.16 | 2.67 | 58000 | 78000 | 32 | 310 | Relatório de uma Subestação Real | 2101.1071 | 12275 | 2122.06 | 12335 | 0.9972% | 0.4888%
QIE1 | 0.22 | HCB | 1050 | 480 | 150 | 3.9 | 1.56 | 1.31 | 270 | 450 | 32 | 310 | Relatório de uma Subestação Real | 6.7918 | 728 | 6.7918 | 728.1163 | 0% | 0.01597%
QIE2 | 0.22 | HCB | 460 | 350 | 120 | 3.9 | 1.56 | 1.31 | 40 | 40 | 32 | 310 | Relatório de uma Subestação Real | 1.5774 | 354 | 1.5774 | 354.6991 | 0% | 0.1975%
QIE3 | 0.22 | HCB | 620 | 500 | 150 | 3.9 | 1.56 | 1.31 | 40 | 40 | 32 | 310 | Relatório de uma Subestação Real | 1.6551 | 363 | 1.6551 | 363.2058 | 0% | 0.05669%
QIE4 | 0.22 | HCB | 620 | 500 | 150 | 3.9 | 1.64 | 1.42 | 40 | 40 | 32 | 310 | Relatório de uma Subestação Real | 1.6551 | 363 | 1.6551 | 363.2058 | 0% | 0.05669%
QIE5 | 0.22 | HCB | 1440 | 490 | 120 | 1.9 | 0.75 | 0.63 | 8500 | 9700 | 32 | 310 | Relatório de uma Subestação Real | 61.1596 | 2149 | 61.9769 | 2136.4599 | 1.336% | 0.5835%
QIE6 | 0.22 | HCB | 2200 | 740 | 520 | 1.8 | 0.71 | 0.6 | 9000 | 9900 | 32 | 310 | Relatório de uma Subestação Real | 60.3945 | 2136 | 60.3945 | 2136.4599 | 0% | 0.02153%
QIE7 | 0.22 | HCB | 1440 | 490 | 120 | 1.8 | 0.71 | 0.6 | 18000 | 22000 | 29.8 | 310 | Relatório de uma Subestação Real | 125.4403 | 3062 | 125.4388 | 3062.4326 | 0.001196% | 0.01413%
QIE8 | 0.22 | HCB | 1440 | 490 | 120 | 1.9 | 0.75 | 0.63 | 960 | 2560 | 32 | 310 | Relatório de uma Subestação Real | 15.449 | 1092 | 15.6558 | 1098.6682 | 1.339% | 0.6106%
QDCA3 | 0.22 | HCB | 800 | 600 | 230 | 3.9 | 1.56 | 1.31 | 660 | 1860 | 32 | 310 | Relatório de uma Subestação Real | 24.8721 | 1380 | 24.8721 | 1380 | 0% | 0%
QDG ADM | 0.22 | HCB | 1880 | 1600 | 460 | 9.7 | 4.03 | 3.4 | 30000 | 38000 | 32 | 310 | Relatório de uma Subestação Real | 1278.369 | 9610 | 1278.3689 | 9610.1169 | 7.822e-06% | 0.001216%
QDL1 | 0.22 | HCB | 870 | 450 | 150 | 9.7 | 4.03 | 3.4 | 95 | 95 | 32 | 310 | Relatório de uma Subestação Real | 4.1301 | 569 | 4.1301 | 569.8793 | 0% | 0.1545%
QDL2 | 0.22 | HCB | 720 | 450 | 150 | 9.7 | 4.03 | 3.4 | 95 | 95 | 32 | 310 | Relatório de uma Subestação Real | 4.1848 | 573 | 4.1847 | 573.5849 | 0.00239% | 0.1021%
QDL3 | 0.22 | HCB | 720 | 450 | 150 | 9.7 | 4.03 | 3.4 | 95 | 95 | 32 | 310 | Relatório de uma Subestação Real | 4.1848 | 573 | 4.1847 | 573.5849 | 0.00239% | 0.1021%
QDL4 | 0.22 | HCB | 720 | 450 | 150 | 9.7 | 4.03 | 3.4 | 95 | 95 | 32 | 310 | Relatório de uma Subestação Real | 4.1848 | 573 | 4.1847 | 573.5849 | 0.00239% | 0.1021%
QE-VAC-01 | 0.22 | HCB | 1880 | 790 | 360 | 7.7 | 3.16 | 2.67 | 40 | 40 | 32 | 310 | Relatório de uma Subestação Real | 3.1832 | 501 | 3.1832 | 501.2723 | 0% | 0.05435%
QD Oficina | 0.22 | HCB | 1460 | 500 | 110 | 3.1 | 1.28 | 1.1 | 950 | 1600 | 32 | 310 | Relatório de uma Subestação Real | 16.4253 | 1124 | 16.4252 | 1124.9438 | 0.0006088% | 0.08397%
QAE-Estufa Fria | 0.22 | HCB | 500 | 390 | 100 | 3.1 | 1.23 | 1.04 | 100 | 100 | 32 | 310 | Relatório de uma Subestação Real | 1.2727 | 319 | 1.2726 | 319.1088 | 0.007857% | 0.03411%
CC3 | 13.8 | HCB | 1244.6 | 1230 | 2000 | 0.,59 | 0.53 | 0.52 | 100 | 100 | 152 | 310 | Relatório de uma Subestação Real | 0.688 | 220 | 0.6802 | 220.1372 | 1.134% | 0.06236%
CC2 | 13.8 | HCB | 1244.6 | 1240 | 2560 | 0.585 | 0.53 | 0.52 | 400 | 410 | 145.7 | 310 | Relatório de uma Subestação Real | 2.7026 | 505 | 2.7026 | 505.9177 | 0% | 0.1817%
CC2 | 13.8 | HCB | 1244.6 | 1240 | 2560 | 0.585 | 0.53 | 0.52 | 400 | 410 | 145.7 | 480 | Relatório de uma Subestação Real | 1.3092 | 505 | 1.3092 | 505.9177 | 0% | 0.1817%
CC2 | 13.8 | HCB | 1244.6 | 1240 | 2560 | 0.585 | 0.53 | 0.52 | 400 | 410 | 145.7 | 1100 | Relatório de uma Subestação Real | 0.3311 | 505 | 0.33114 | 505.9177 | 0.01208% | 0.1817%
CC2 | 13.8 | HCB | 1244.6 | 1240 | 2560 | 0.585 | 0.53 | 0.52 | 400 | 410 | 145.7 | 2000 | Relatório de uma Subestação Real | 0.1229 | 505 | 0.1229 | 505.9177 | 0% | 0.1817%
CC1 | 13.8 | HCB | 2850 | 1240 | 2560 | 0.585 | 0.53 | 0.52 | 400 | 410 | 145.7 | 310 | Relatório de uma Subestação Real | 2.7026 | 505 | 2.7026 | 505.9177 | 0% | 0.1817%
Cubiculo SC2167 | 13.8 | VCB | 1780 | 1080 | 900 | 0.585 | 0.54 | 0.53 | 90 | 90 | 152 | 310 | Relatório de uma Subestação Real | 0.3555 | 142 | 0.3494 | 141.1 | 1.716% | 0.6338%
Cubiculo SC2167 | 13.8 | VCB | 1780 | 1080 | 900 | 0.585 | 0.54 | 0.53 | 90 | 90 | 152 | 480 | Relatório de uma Subestação Real | 0.1791 | 142 | 0.176 | 141.1 | 1.731% | 0.6338%
Cubiculo SC2167 | 13.8 | VCB | 1780 | 1080 | 900 | 0.585 | 0.54 | 0.53 | 90 | 90 | 152 | 1100 | Relatório de uma Subestação Real | 0.0488 | 142 | 0.04795 | 141.1 | 1.742% | 0.6338%
Cubiculo SC2167 | 13.8 | VCB | 1780 | 1080 | 900 | 0.585 | 0.54 | 0.53 | 90 | 90 | 152 | 2000 | Relatório de uma Subestação Real | 0.0191 | 142 | 0.018779 | 141.1 | 1.681% | 0.6338%
Cubiculo SC2247 | 13.8 | VCB | 1780 | 1080 | 900 | 0.585 | 0.54 | 0.53 | 30 | 30 | 32 | 310 | Relatório de uma Subestação Real | 0.3555 | 142 | 0.3555 | 142.6941 | 0% | 0.4888%
Cubiculo SC2157 | 13.8 | VCB | 1780 | 1080 | 900 | 0.585 | 0.54 | 0.53 | 30 | 30 | 32 | 310 | Relatório de uma Subestação Real | 0.3555 | 142 | 0.3555 | 142.6941 | 0% | 0.4888%
Cubiculo SC2257 | 13.8 | VCB | 1780 | 1080 | 900 | 0.585 | 0.54 | 0.53 | 30 | 30 | 32 | 310 | Relatório de uma Subestação Real | 0.3555 | 142 | 0.3555 | 142.6941 | 0% | 0.4888%
Cubiculo SC2147 | 13.8 | VCB | 1244 | 1080 | 900 | 0.585 | 0.54 | 0.53 | 90 | 90 | 152 | 310 | Relatório de uma Subestação Real | 0.352 | 142 | 0.3522 | 141.8522 | 0.05682% | 0.1041%
Cubiculo SC2015 | 13.8 | VCB | 2660 | 1230 | 1500 | 0.585 | 0.54 | 0.53 | 90 | 90 | 175 | 310 | Relatório de uma Subestação Real | 0.3511 | 141 | 0.35106 | 141.54 | 0.01139% | 0.383%
Cubiculo SC2015 | 13.8 | VCB | 2660 | 1230 | 1500 | 0.585 | 0.54 | 0.53 | 90 | 90 | 175 | 480 | Relatório de uma Subestação Real | 0.1769 | 141 | 0.17686 | 141.54 | 0.02261% | 0.383%
Cubiculo SC2015 | 13.8 | VCB | 2660 | 1230 | 1500 | 0.585 | 0.54 | 0.53 | 90 | 90 | 175 | 1100 | Relatório de uma Subestação Real | 0.0482 | 141 | 0.04818 | 141.54 | 0.04149% | 0.383%
Cubiculo SC2015 | 13.8 | VCB | 2660 | 1230 | 1500 | 0.585 | 0.54 | 0.53 | 90 | 90 | 175 | 2000 | Relatório de uma Subestação Real | 0.0189 | 141 | 0.01887 | 141.54 | 0.1587% | 0.383%
Cubiculo SC2017 | 13.8 | VCB | 2660 | 1230 | 1500 | 0.585 | 0.54 | 0.53 | 30 | 30 | 32 | 310 | Relatório de uma Subestação Real | 0.3511 | 141 | 0.3511 | 141.5651 | 0% | 0.4008%
QAS | 0.48 | HCB | 2130 | 690 | 760 | 5.28 | 3.66 | 3.151 | 100 | 100 | 32 | 310 | Relatório de uma Subestação Real | 3.711 | 540 | 3.711 | 540.6244 | 0% | 0.1156%
QAN | 0.48 | HCB | 2130 | 690 | 760 | 6.88 | 4.81 | 4.15 | 90 | 90 | 32 | 310 | Relatório de uma Subestação Real | 4.4432 | 590 | 4.4363 | 590.3181 | 0.1553% | 0.05392%
QS1 | 0.48 | HCB | 2300 | 1000 | 770 | 5.28 | 3.66 | 3.16 | 9000 | 11000 | 32 | 310 | Relatório de uma Subestação Real | 344.0987 | 5034 | 344.0987 | 5034.4694 | 2.906e-06% | 0.009325%
QS2 | 0.48 | HCB | 1244.6 | 1000 | 770 | 5.28 | 3.66 | 3.16 | 90 | 90 | 32 | 310 | Relatório de uma Subestação Real | 3.2834 | 508 | 3.2834 | 508.98 | 0.0001523% | 0.1929%
QN1 | 0.48 | HCB | 2300 | 1000 | 770 | 6.89 | 5.04 | 4.42 | 100 | 100 | 32 | 310 | Relatório de uma Subestação Real | 4.8534 | 617 | 4.8534 | 617.03 | 0.000783% | 0.004862%
QN2 | 0.48 | HCB | 2300 | 1000 | 770 | 6.89 | 5.04 | 4.42 | 100 | 100 | 32 | 310 | Relatório de uma Subestação Real | 4.8534 | 617 | 4.8534 | 617.03 | 0.0008036% | 0.004862%
QN2 | 0.48 | HCB | 2300 | 1000 | 770 | 6.89 | 5.04 | 4.42 | 100 | 100 | 32 | 480 | Relatório de uma Subestação Real | 1.998 | 617 | 1.998 | 617.03 | 0.002002% | 0.004862%
QN2 | 0.48 | HCB | 2300 | 1000 | 770 | 6.89 | 5.04 | 4.42 | 100 | 100 | 32 | 1100 | Relatório de uma Subestação Real | 0.3711 | 617 | 0.37109 | 617.03 | 0.002695% | 0.004862%
QN2 | 0.48 | HCB | 2300 | 1000 | 770 | 6.89 | 5.04 | 4.42 | 100 | 100 | 32 | 2000 | Relatório de uma Subestação Real | 0.1103 | 617 | 0.11026 | 617.03 | 0.03626% | 0.004862%
QF1 | 0.48 | HCB | 2300 | 1000 | 770 | 5.22 | 3.62 | 3.12 | 90 | 90 | 32 | 310 | Relatório de uma Subestação Real | 3.2435 | 505 | 3.2435 | 505.93 | 6.166e-05% | 0.1842%
QF1 | 0.48 | HCB | 2300 | 1000 | 770 | 5.22 | 3.62 | 3.12 | 90 | 90 | 32 | 480 | Relatório de uma Subestação Real | 1.3352 | 505 | 1.3352 | 505.93 | 0.002996% | 0.1842%
QF1 | 0.48 | HCB | 2300 | 1000 | 770 | 5.22 | 3.62 | 3.12 | 90 | 90 | 32 | 1100 | Relatório de uma Subestação Real | 0.248 | 505 | 0.248 | 505.93 | 0% | 0.1842%
QF1 | 0.48 | HCB | 2300 | 1000 | 770 | 5.22 | 3.62 | 3.12 | 90 | 90 | 32 | 2000 | Relatório de uma Subestação Real | 0.0737 | 505 | 0.073686 | 505.93 | 0.019% | 0.1842%
QFE1 | 0.48 | HCB | 1920 | 790 | 460 | 5.28 | 3.66 | 3.16 | 95 | 95 | 32 | 310 | Relatório de uma Subestação Real | 3.5049 | 525 | 3.5049 | 525.6165 | 0% | 0.1174%
QFE2 | 0.48 | HCB | 1920 | 790 | 460 | 5.28 | 3.82 | 3.34 | 95 | 95 | 32 | 310 | Relatório de uma Subestação Real | 3.5049 | 525 | 3.5049 | 525.6165 | 0% | 0.1174%
QFE3 | 0.48 | HCB | 1800 | 810 | 550 | 5.28 | 3.82 | 3.34 | 100 | 100 | 32 | 310 | Relatório de uma Subestação Real | 3.6852 | 538 | 3.6851 | 538.7665 | 0.002714% | 0.1425%
QFE4 | 0.48 | HCB | 1200 | 790 | 280 | 5.28 | 3.82 | 3.34 | 100 | 100 | 32 | 310 | Relatório de uma Subestação Real | 3.6989 | 539 | 3.6989 | 539.7498 | 0% | 0.1391%
QDN2 | 0.48 | HCB | 1920 | 790 | 460 | 6.88 | 4.81 | 4.15 | 100 | 100 | 32 | 310 | Relatório de uma Subestação Real | 4.9081 | 620 | 4.9004 | 619.9743 | 0.1569% | 0.004145%
QDN3 | 0.48 | HCB | 1920 | 790 | 460 | 6.88 | 4.81 | 4.15 | 100 | 100 | 32 | 310 | Relatório de uma Subestação Real | 4.9081 | 620 | 4.9004 | 619.9743 | 0.1569% | 0.004145%
QDN4 | 0.48 | HCB | 1920 | 790 | 460 | 6.88 | 4.81 | 4.15 | 100 | 100 | 32 | 310 | Relatório de uma Subestação Real | 4.9081 | 620 | 4.9004 | 619.9743 | 0.1569% | 0.004145%
QFN2 | 0.48 | VCB | 990 | 840 | 220 | 6.88 | 5.04 | 4.42 | 35 | 35 | 32 | 310 | Relatório de uma Subestação Real | 1.7068 | 386 | 1.7041 | 386.0792 | 0.1582% | 0.02052%
QFN3 | 0.48 | HCB | 1460 | 500 | 150 | 6.88 | 5.04 | 4.42 | 100 | 100 | 32 | 310 | Relatório de uma Subestação Real | 5.0528 | 629 | 5.0448 | 628.9097 | 0.1583% | 0.01436%
QFN4 | 0.48 | VCB | 600 | 670 | 220 | 6.88 | 5 | 4.4 | 100 | 100 | 32 | 310 | Relatório de uma Subestação Real | 2.0284 | 430 | 2.0251 | 430.12 | 0.1627% | 0.02791%
QFN4 | 0.48 | VCB | 600 | 670 | 220 | 6.88 | 5 | 4.4 | 100 | 100 | 32 | 480 | Relatório de uma Subestação Real | 1.0086 | 430 | 1.007 | 430.12 | 0.1596% | 0.02791%
QFN4 | 0.48 | VCB | 600 | 670 | 220 | 6.88 | 5 | 4.4 | 100 | 100 | 32 | 1100 | Relatório de uma Subestação Real | 0.268 | 430 | 0.26761 | 430.12 | 0.1451% | 0.02791%
QFN4 | 0.48 | VCB | 600 | 670 | 220 | 6.88 | 5 | 4.4 | 100 | 100 | 32 | 2000 | Relatório de uma Subestação Real | 0.103 | 430 | 0.1029 | 430.12 | 0.09709% | 0.02791%
QDFB | 0.48 | HCB | 14600 | 500 | 150 | 6.88 | 4.81 | 4.15 | 95 | 95 | 32 | 310 | Relatório de uma Subestação Real | 4.8001 | 613 | 4.7926 | 613.2178 | 0.1562% | 0.03553%
PNL GD1 | 0.48 | VCB | 1890 | 800 | 600 | 1.5 | 1.02 | 0.89 | 1400 | 1900 | 32 | 310 | Relatório de uma Subestação Real | 5.3168 | 786 | 5.3168 | 786.88 | 0.0001881% | 0.112%
PNL GD1 | 0.48 | VCB | 1890 | 800 | 600 | 1.5 | 1.02 | 0.89 | 1400 | 1900 | 32 | 480 | Relatório de uma Subestação Real | 2.6438 | 786 | 2.6438 | 786.88 | 0% | 0.112%
PNL GD1 | 0.48 | VCB | 1890 | 800 | 600 | 1.5 | 1.02 | 0.89 | 1400 | 1900 | 32 | 1100 | Relatório de uma Subestação Real | 0.7026 | 786 | 0.7025 | 786.88 | 0.01423% | 0.112%
PNL GD1 | 0.48 | VCB | 1890 | 800 | 600 | 1.5 | 1.02 | 0.89 | 1400 | 1900 | 32 | 2000 | Relatório de uma Subestação Real | 0.2703 | 786 | 0.27027 | 786.88 | 0.0111% | 0.112%
Cabos de Entrada | 0.48 | VCB | 770 | 550 | 400 | 10.51 | 7.886 | 6.914 | 787 | 787 | 30 | 609.6 | SATO, 2022 | 8.3 | 2051 | 8.34 | 2050.956 | 0.4819% | 0.002145%
DJ-02AB | 0.48 | HCB | 350 | 300 | 400 | 10.51 | 7.51 | 6.474 | 102 | 102 | 30 | 609.6 | SATO, 2022 | 2.2 | 821 | 2.1937 | 820.553 | 0.2864% | 0.05445%
DJ-02C | 0.48 | HCB | 350 | 300 | 400 | 10.51 | 7.51 | 6.474 | 81.5 | 81.5 | 30 | 609.6 | SATO, 2022 | 1.8 | 735 | 1.7528 | 734.69 | 2.622% | 0.04218%
Gaveta_TP | 0.48 | HCB | 270 | 550 | 400 | 10.51 | 7.32 | 6.31 | 81.5 | 81.5 | 36 | 457.2 | SATO, 2022 | 3.3 | 749 | 3.2698 | 749.13 | 0.9152% | 0.01736%
Gaveta_Dem | 0.48 | HCB | 130 | 550 | 400 | 10.51 | 7.32 | 6.31 | 81.5 | 81.5 | 36 | 457.2 | SATO, 2022 | 3.3 | 749 | 3.2698 | 749.13 | 0.9152% | 0.01736%
Cabos_Saída | 0.48 | HCB | 2100 | 390 | 400 | 10.51 | 7.32 | 6.31 | 81.5 | 81.5 | 36 | 457.2 | SATO, 2022 | 3 | 723 | 3.04 | 722.98 | 1.333% | 0.002766%
Annex D.1 | 4.16 | VCB | 1143 | 762 |  | 15 | 12.979 | 12.675 | 197 | 223 | 104 | 914.4 | IEEE 1584, 2018 | 3.19 | 1704 | 3.1891 | 1704.19 | 0.02727% | 0.01115%
Annex D.2 | 0.48 | VCB | 610 | 610 | 254 | 45 | 28.79 | 25.24 | 61.3 | 319 | 32 | 609.6 | IEEE 1584, 2018 | 12.7 | 2669 | 12.7047 | 2668.919 | 0.03701% | 0.003035%
QD-02 | 13.8 | VCB | 592 | 568 | 722 | 14.88 | 13.9 | 13.73 | 675 | 675 | 152 | 914.4 | Pauli; Bartsch, 2021 | 13.93 | 4366 | 13.918 | 4364.1975 | 0.08615% | 0.04128%
CCM-MT | 4.16 | VCB | 480 | 690 | 380 | 5.13 | 4.52 | 4.42 | 535 | 545 | 104 | 914.4 | Pauli; Bartsch, 2021 | 3.39 | 1771 | 3.384 | 1770.293 | 0.177% | 0.03992%
CCM-BT | 0.48 | VCB | 480 | 690 | 380 | 31.142 | 22.71 | 19.92 | 635 | 735 | 25 | 457.2 | Pauli; Bartsch, 2021 | 33.46 | 3669 | 33.456 | 3668.98 | 0.01195% | 0.0005451%
QD-02 | 13.8 | VCB | 592 | 568 | 722 | 14.88 | 13.9 | 13.73 | 77 | 77 | 152 | 914.4 | Pauli; Bartsch, 2021 | 1.59 | 1093 | 1.5877 | 1093.039 | 0.1447% | 0.003568%
CCM-MT | 4.16 | VCB | 480 | 690 | 380 | 5.13 | 4.52 | 4.42 | 77 | 77 | 104 | 914.4 | Pauli; Bartsch, 2021 | 0.49 | 515 | 0.487 | 514.56 | 0.6122% | 0.08544%
CCM-BT | 0.48 | VCB | 480 | 690 | 380 | 31.142 | 22.71 | 19.92 | 77 | 77 | 25 | 457.2 | Pauli; Bartsch, 2021 | 3.98 | 967 | 3.9751 | 967.4253 | 0.1231% | 0.04398%

## CC
Dados de Entrada | [5 empty] | Resultado | [5 empty] | Comparação
[12 empty] | Media Todos | 74.34% | Média DOAN | 0.3226%
[6 empty] | Fonte | Metodologia | Energia Incidente | Limite Seguro de Aproximação | Software dos Autores |  | DP Todos | 88.28% | DP DOAN | 1.116%
Equipamento | Invólucro (FECHADO/ABERTO) | Tensão Nominal [kV] | Icc [kA] | TIcc [ms] | Distancia de Trabalho [mm] |  |  |  |  | Energia Incidente | Limite Seguro de Aproximação | Erro Percentual Energia Incidente | Erro Percentual no Limite Seguro de Aproximação
Banco de Baterias 1 | Aberto | 0.125 | 6 | 2000 | 455 | Relatório de uma Subestação Real | NFPA 70E | 3.6228 | 1200 | 3.6228 | 2500 | 0% | 108.3%
Banco de Baterias 2 | Aberto | 0.125 | 6 | 2000 | 455 | Relatório de uma Subestação Real | NFPA 70E | 3.6228 | 1200 | 3.6228 | 2500 | 0% | 108.3%
Banco de Baterias 1 | Aberto | 0.048 | 2.4 | 2000 | 455 | Relatório de uma Subestação Real | NFPA 70E | 0.5565 | 900 | 0.5565 | 1200 | 0% | 33.33%
Banco de Baterias 2 | Aberto | 0.048 | 2.4 | 2000 | 455 | Relatório de uma Subestação Real | NFPA 70E | 0.5565 | 900 | 0.5565 | 1200 | 0% | 33.33%
QDCC1-1 | Fechado | 0.125 | 6 | 30 | 310 | Relatório de uma Subestação Real | Stokes and Oppenlander | 0.1638 | 1200 | 0.3511 | 1800 | 114.3% | 50%
QDCC1-2 | Fechado | 0.125 | 6 | 30 | 310 | Relatório de uma Subestação Real | Stokes and Oppenlander | 0.1609 | 1200 | 0.3511 | 1800 | 118.2% | 50%
QDCC1A | Fechado | 0.125 | 6 | 30 | 310 | Relatório de uma Subestação Real | Stokes and Oppenlander | 0.1638 | 1200 | 0.3511 | 1800 | 114.3% | 50%
QDCC1B | Fechado | 0.125 | 6 | 30 | 310 | Relatório de uma Subestação Real | Stokes and Oppenlander | 0.1638 | 1200 | 0.3511 | 1800 | 114.3% | 50%
QDCCE | Fechado | 0.125 | 6 | 40 | 310 | Relatório de uma Subestação Real | Stokes and Oppenlander | 0.2184 | 1200 | 0.4682 | 1800 | 114.4% | 50%
QDCCE1 | Fechado | 0.125 | 6 | 40 | 310 | Relatório de uma Subestação Real | Stokes and Oppenlander | 0.2184 | 1200 | 0.4682 | 1800 | 114.4% | 50%
CIF | Fechado | 0.048 | 2.4 | 40 | 310 | Relatório de uma Subestação Real | Stokes and Oppenlander | 0.0335 | 900 | 0.072 | 1200 | 114.9% | 33.33%
QDCC | Fechado | 0.048 | 2.4 | 10 | 310 | Relatório de uma Subestação Real | Stokes and Oppenlander | 0.0335 | 900 | 0.018 | 1200 | 46.27% | 33.33%
Caso 1 – 60 A | Fechado | 0.125 | 2 | 2000 | 450 | O Setor Eletrico Ed.199 | NFPA 70E | 3.56 | NA | 3.7037 | 1443.38 | 4.037% | NA
Caso 2 – 800 A | Fechado | 1 | 0.881 | 2000 | 450 | O Setor Eletrico Ed.199 | NFPA 70E | 13.05 | NA | 13.0518 | 2709.551 | 0.01418% | NA
Caso 1 – 60 A | Fechado | 0.125 | 2 | 2000 | 450 | O Setor Eletrico Ed.199 | EPRI | 3.18 | NA | 3.7037 | 1443.38 | 16.47% | NA
Caso 2 – 800 A | Fechado | 1 | 0.881 | 2000 | 450 | O Setor Eletrico Ed.199 | EPRI | 3.54 | NA | 13.0518 | 2709.551 | 268.7% | NA
Single String System | Aberto | 0.258 | 18.7 | 400 | 457 | Ammerman; Gammon; Sen; Nelson. DC-Arc Models and Incident-Energy Calculations. IEEE, 2010 | Própria | 4 | NA | 4.62 | 2836 | 15.5% | NA
Single String System | Aberto | 0.258 | 18.7 | 800 | 457 | Ammerman; Gammon; Sen; Nelson. DC-Arc Models and Incident-Energy Calculations. IEEE, 2010 | Própria | 8 | NA | 9.24 | 4010 | 15.5% | NA
Single String System | Aberto | 0.258 | 18.7 | 1400 | 457 | Ammerman; Gammon; Sen; Nelson. DC-Arc Models and Incident-Energy Calculations. IEEE, 2010 | Própria | 14 | NA | 16.2 | 5305 | 15.71% | NA
Single String System | Aberto | 0.258 | 18.7 | 2000 | 457 | Ammerman; Gammon; Sen; Nelson. DC-Arc Models and Incident-Energy Calculations. IEEE, 2010 | Própria | 21 | NA | 23.1 | 6340 | 10% | NA
Double String System | Aberto | 0.258 | 39 | 400 | 457 | Ammerman; Gammon; Sen; Nelson. DC-Arc Models and Incident-Energy Calculations. IEEE, 2010 | Própria | 9 | NA | 9.64 | 4095 | 7.111% | NA
Double String System | Aberto | 0.258 | 39 | 800 | 457 | Ammerman; Gammon; Sen; Nelson. DC-Arc Models and Incident-Energy Calculations. IEEE, 2010 | Própria | 17.5 | NA | 19.27 | 5791 | 10.11% | NA
Double String System | Aberto | 0.258 | 39 | 1400 | 457 | Ammerman; Gammon; Sen; Nelson. DC-Arc Models and Incident-Energy Calculations. IEEE, 2010 | Própria | 32 | NA | 33.73 | 7661 | 5.406% | NA
Double String System | Aberto | 0.258 | 39 | 2000 | 457 | Ammerman; Gammon; Sen; Nelson. DC-Arc Models and Incident-Energy Calculations. IEEE, 2010 | Própria | 43.5 | NA | 48.18 | 9156 | 10.76% | NA
TestBox | Fechado | 0.13 | 1.893 | 200 | 457.2 | Weimann, Analytical and Experimental Validation for DC Arc Flash Models. Table 7. University of Pittsburgh. 2020 | DOAN | 0.353 | NA | 0.35319 | 1200 | 0.05255% | NA
TestBox | Fechado | 0.13 | 1.893 | 200 | 457.2 | Weimann, Analytical and Experimental Validation for DC Arc Flash Models. Table 7. University of Pittsburgh. 2020 | Paukert | 0.164 | NA | 0.35319 | 1200 | 115.4% | NA
TestBox | Fechado | 0.13 | 1.893 | 200 | 457.2 | Weimann, Analytical and Experimental Validation for DC Arc Flash Models. Table 7. University of Pittsburgh. 2020 | Stokes and Oppenlander | 0.17 | NA | 0.35319 | 1200 | 107.8% | NA
TestBox | Fechado | 0.13 | 7.4 | 200 | 457.2 | Weimann, Analytical and Experimental Validation for DC Arc Flash Models. Table 7. University of Pittsburgh. 2020 | DOAN | 1.381 | NA | 1.3807 | 2500 | 0.02529% | NA
TestBox | Fechado | 0.13 | 7.4 | 200 | 457.2 | Weimann, Analytical and Experimental Validation for DC Arc Flash Models. Table 7. University of Pittsburgh. 2020 | Paukert | 0.666 | NA | 1.3807 | 2500 | 107.3% | NA
TestBox | Fechado | 0.13 | 7.4 | 200 | 457.2 | Weimann, Analytical and Experimental Validation for DC Arc Flash Models. Table 7. University of Pittsburgh. 2020 | Stokes and Oppenlander | 0.66 | NA | 1.3807 | 2500 | 109.2% | NA
TestBox | Fechado | 0.13 | 12 | 200 | 457.2 | Weimann, Analytical and Experimental Validation for DC Arc Flash Models. Table 7. University of Pittsburgh. 2020 | DOAN | 2.239 | NA | 2.2389 | 2500 | 0.004774% | NA
TestBox | Fechado | 0.13 | 12 | 200 | 457.2 | Weimann, Analytical and Experimental Validation for DC Arc Flash Models. Table 7. University of Pittsburgh. 2020 | Paukert | 1.078 | NA | 2.2389 | 2500 | 107.7% | NA
TestBox | Fechado | 0.13 | 12 | 200 | 457.2 | Weimann, Analytical and Experimental Validation for DC Arc Flash Models. Table 7. University of Pittsburgh. 2020 | Stokes and Oppenlander | 1.055 | NA | 2.2389 | 2500 | 112.2% | NA
TestBox | Fechado | 0.13 | 15.8 | 200 | 457.2 | Weimann, Analytical and Experimental Validation for DC Arc Flash Models. Table 7. University of Pittsburgh. 2020 | DOAN | 2.948 | NA | 2.9479 | 2500 | 0.004199% | NA
TestBox | Fechado | 0.13 | 15.8 | 200 | 457.2 | Weimann, Analytical and Experimental Validation for DC Arc Flash Models. Table 7. University of Pittsburgh. 2020 | Paukert | 1.074 | NA | 2.9479 | 2500 | 174.5% | NA
TestBox | Fechado | 0.13 | 15.8 | 200 | 457.2 | Weimann, Analytical and Experimental Validation for DC Arc Flash Models. Table 7. University of Pittsburgh. 2020 | Stokes and Oppenlander | 1.292 | NA | 2.9479 | 2500 | 128.2% | NA
TestBox | Fechado | 0.13 | 20.9 | 200 | 457.2 | Weimann, Analytical and Experimental Validation for DC Arc Flash Models. Table 7. University of Pittsburgh. 2020 | DOAN | 3.901 | NA | 3.8994 | 2500 | 0.04086% | NA
TestBox | Fechado | 0.13 | 20.9 | 200 | 457.2 | Weimann, Analytical and Experimental Validation for DC Arc Flash Models. Table 7. University of Pittsburgh. 2020 | Paukert | 1.323 | NA | 3.8994 | 2500 | 194.7% | NA
TestBox | Fechado | 0.13 | 20.9 | 200 | 457.2 | Weimann, Analytical and Experimental Validation for DC Arc Flash Models. Table 7. University of Pittsburgh. 2020 | Stokes and Oppenlander | 1.502 | NA | 3.8994 | 2500 | 159.6% | NA
TestBox | Fechado | 0.13 | 27.5 | 200 | 457.2 | Weimann, Analytical and Experimental Validation for DC Arc Flash Models. Table 7. University of Pittsburgh. 2020 | DOAN | 5.131 | NA | 5.1308 | 2500 | 0.003937% | NA
TestBox | Fechado | 0.13 | 27.5 | 200 | 457.2 | Weimann, Analytical and Experimental Validation for DC Arc Flash Models. Table 7. University of Pittsburgh. 2020 | Paukert | 2.401 | NA | 5.1308 | 2500 | 113.7% | NA
TestBox | Fechado | 0.13 | 27.5 | 200 | 457.2 | Weimann, Analytical and Experimental Validation for DC Arc Flash Models. Table 7. University of Pittsburgh. 2020 | Stokes and Oppenlander | 2.316 | NA | 5.1308 | 2500 | 121.5% | NA
Battery Unit | Aberto | 0.5712 | 9 | 18 | 800 | Guide APPLICATION, ABB. 2023 | Não informado | 0.072 | NA | 0.07223 | 2500 | 0.3194% | NA
Battery Unit | Aberto | 0.5712 | 9 | 80 | 800 | Guide APPLICATION, ABB. 2023 | Não informado | 0.4 | NA | 0.32 | 2500 | 20% | NA
PV System | Fechado | 0.6 | 1.734 | 2000 | 457.2 | Comparative Study of DC Arc Flash Analysis Methods in ETAP, ETAP Software. jul, 2016 | DOAN | 14.93 | NA | 14.9317 | 2945 | 0.01139% | NA
PV System | Fechado | 0.6 | 1.734 | 2000 | 457.2 | Comparative Study of DC Arc Flash Analysis Methods in ETAP, ETAP Software. jul, 2016 | Paukert | 3.36 | NA | 14.9317 | 2945 | 344.4% | NA
PV System | Fechado | 0.6 | 1.734 | 2000 | 457.2 | Comparative Study of DC Arc Flash Analysis Methods in ETAP, ETAP Software. jul, 2016 | Stokes and Oppenlander | 3.34 | NA | 14.9317 | 2945 | 347.1% | NA